Application No.:  326118

Equipment Category – Heater - Refinery

| 1. GENERAL INFORMATION |  | DATE: 9/9/1999 |
| --- | --- | --- |
| a. manufacturer: Howe Baker Engineers |
| b. type: Hydrogen reforming furnace | c. model: |
| d. style: |
| e. applicable aqmd regulation xi rules: |
| f. cost: $ ( ) source of cost data: |
| g. operating schedule: 24 hrs/day 7 days/wk 52 wks/yr |

| 2. EQUIPMENT INFORMATION |  | App. No.: 326118 |
| --- | --- | --- |
| A. FUNCTION: This heater is part of a hydrogen plant at a refinery. It heats hydrocarbon feed streams to reform them with steam to H2 and CO2. |
| B. maximum Heat Input: 460 MMBtu/hr | C. maximum throughput: |
| D. burner information: no.: 72 type: Callidus Model LE-CRG Lo-NOx |
| e. primary fuel: Pressure swing absorption off gas (lo-Btu) & refinery gas | f. other fuel: Natural gas |
| g. operating conditions: |

| 3. COMPANY INFORMATION |  | App. No.: 326118 |
| --- | --- | --- |
| A. NAME: TOSCO Refining Co. |
| B. ADDRESS: 1660 W. Anaheim St. CITY: Wilmington STATE: CA ZIP: 90744 |
| C. CONTACT PERSON: Miles Heller | D. PHONE NO.: 310.952.6120 |

| 4. PERMIT INFORMATION |  | App. No.: 326118 |
| --- | --- | --- |
| A. AGENCY: SCAQMD |
| B. AGENCY CONTACT PERSON: Ngoc Tran | C. PHONE NO.: 909.396.2606 |
| D. PERMIT TO CONSTRUCT INFORMATION: P/C NO.: 290738 ISSUANCE DATE: 7/24/1994 |
| E. START-UP DATE: 4/95 |
| F. PERMIT TO OPERATE INFORMATION: P/O NO.: ISSUANCE DATE: |

| 5. EMISSION INFORMATION |  | App. No.: 326118 |
| --- | --- | --- |
| A. PERMIT |
| A1. PERMIT LIMIT: NOx: 7 ppmv; NH3: 20 ppmv; each dry, corrected to 3% O2 and averaged over 15 minutes; SOx: 11.1 lbs/hr; fuel total sulfur content: 100 ppm as H2S. Exceptions to NOx limit: startup and shutdowns, 150 hours of refractory dry out, and when heater exhaust is < 600 degrees F (to avoid ammonium bisulphate deposits.) |
| A2. bact/lAer DETERMINATION: Compliance with above limits |
| B. CONTROL TECHNOLOGY |
| B1. MANUFACTURER/SUPPLIER: Peerless Mfg. Co. |
| B2. TYPE: Selective catalytic reduction (SCR) with acqueous ammonia injection |
| B3. DESCRIPTION: NOx is chemically reduced to N2 by the reducing agent NH3 in the presence of a Cormetech, Inc. catalyst. |
| B4. CONTROL EQUIPMENT PERMIT APPLICATION DATA: P/C NO.: 290739 ISSUANCE DATE: 7/22/1994 P/O NO.: ISSUANCE DATE: |
| B5. WASTE AIR FLOW TO CONTROL EQUIPMENT: FLOW RATE: ACTUAL CONTAMINANT LOADING: BLOWER HP: 700 HP |
| B6. WARRANTY: |
| B7. PRIMARY POLLUTANTS: NOx, SOx, CO, NMHC, PM10 |
| B8. SECONDARY POLLUTANTS: NH3 |
| B9. SPACE REQUIREMENT: Reactor: 16'-5" W x 24'-4" L x 10' H |
| B10. LIMITATIONS: |
| B11. LOCATION OF PRIOR DEMONSTRATION & AGENCY: FACILITY: CONTACT PERSON: PHONE NO.: AGENCY: ADDRESS: CONTACT PERSON: PHONE NO.: |
| B12. OPERATING HISTORY: |
| B13. SOURCE TEST/PERFORMANCE DATA ANALYSIS: DATE OF SOURCE TEST: 10/3/95 CAPTURE EFFICIENCY: 100% DESTRUCTION EFFICIENCY: NOx: >94% OVERALL EFFICEINCY: NOx: >94% PERFORMANCE DATA: Inlet NOx: 38.7 ppmv, dry corrected to 3% O2, 1-hr avg. Outlet NOx: <2.7 ppmv, dry corrected to 3% O2, 1-hr avg. Outlet CO: <6.7 ppmv, dry corrected to 3% O2, 1-hr avg. Outlet SO2: <6.7 ppmv, dry corrected to 3% O2, 1-hr avg.; <3.65 lbs/hr Outlet NH3: 2.7 ppmv, dry corrected to 3% O2, avg. of 3 45-minute tests Outlet NMHC: 6.4 ppmv as methane, dry corrected to 3% O2 Outlet PM10: 0.0011 grains/dscf, 0.65 lbs/hr; EPA Method 201A,front and back half 0.0004 grains/dscf, 0.27 lbs/hr, Corrected for ammonium sulfate |
| B14. SOURCE TEST CONDITIONS/PERFORMANCE DATA: 337 MM Btu/hr heat input |
| C. COST |
| C1. CONTROL EQUIPMENT COST: check if installation cost is included in capital cost CAPITAL: $ INSTALLATION: $ ( ) SOURCE OF COST DATA: |
| C2. ANNUAL OPERATIONAL/MAINTENANCE COST: $ ( ) SOURCE OF COST DATA: |
| D. DEMONSTRATION OF COMPLIANCE |
| D1. STAFF PERMFORMING FIELD EVALUATION: ENGINEER'S NAME: INSPECTOR'S NAME: DATE: |
| D2. COMPLIANCE DEMONSTRATION: Source test and NOx and SOx CEMS |
| D3. VARIANCE: NO. OF VARIANCES: DATES: CAUSES: |
| D4. VIOLATION: NO. OF VIOLATIONS: Two DATES: 5/5/97, 8/8/98 CAUSES: Failure to report a SCR breakdown; Failure to inject NH3 due to a plugging problem |
| D5. FREQUENCY OF MAINTENANCE: |

| 6. COMMENTS |  | App. No.: 326118 |
| --- | --- | --- |