 FORMDROPDOWN 

Application No.:  362396
Equipment Category - Boiler
1.
GENERAL INFORMATION

DATE:   06/08/2001

a.
manufacturer:   Clayton

b.
type:   water tube type
c.
model:   E6100-LNB

d.
style:        

e.
applicable aqmd regulation xi rules:   Rule 1146 for CO (NOx RECLAIM facility)

f.
cost:   $50,000  (1999)
source of cost data:    FORMDROPDOWN 


g.
operating schedule:
24  hrs/day
7  days/wk
52  wks/yr

2.
EQUIPMENT INFORMATION

App. No.:   362396

A.
FUNCTION:   supply hot water

B.
maximum Heat Input:   4.292 mmbtu/hr
C.
maximum throughput:        

D.
burner information:
no.:   1
type:   Clayton, Model UH-29885 

e.
primary fuel:   natural gas
f.
other fuel:   none

g.
operating conditions:   relatively steady-state operation with decreased boiler load late at night 

3.
COMPANY INFORMATION

App. No.:   362396

A.
NAME:   SCHI Santa Monica Beach Hotel Associates

B.
ADDRESS:   1700 Ocean Blvd
CITY:   Santa Monica
STATE:   CA
ZIP:   92680

C.
CONTACT PERSON:   Sam Cala
D.
PHONE NO.:   310-576-3122

4.
PERMIT INFORMATION

App. No.:   362396

A.
AGENCY:   SCAQMD

B.
AGENCY CONTACT PERSON:   Roy Olivares
C.
PHONE NO.:   909-393-2208

D.
PERMIT TO CONSTRUCT INFORMATION:
P/C NO.:   362396
ISSUANCE DATE:   12/2/99

E.
START-UP DATE:
Jan 2000

F.
PERMIT TO OPERATE INFORMATION:
P/O NO.:   Pending
ISSUANCE DATE:        

5.
EMISSION INFORMATION

App. No.:   362396

A.
PERMIT

A1.
PERMIT LIMIT:   NOx =< 12 ppmvd at 3% O2 and CO =< 100 ppmvd at 3% O2

A2.
bact/lAer DETERMINATION:   see above limits

B.
CONTROL TECHNOLOGY

B1.
MANUFACTURER/SUPPLIER:   Clayton

B2.
TYPE:   ultra low-NOx burner, Model UH-29885

B3.
DESCRIPTION:
   The ultra low-NOx burner system achieves low emissions through a combination of improved fuel and air mixing, ultra lean flame design and low flame residence time

B4.
CONTROL EQUIPMENT PERMIT APPLICATION DATA:
P/C NO.:   n/a
ISSUANCE DATE:        


P/O NO.:   n/a
ISSUANCE DATE:        

B5.
WASTE AIR FLOW TO CONTROL EQUIPMENT:
FLOW RATE:   n/a
ACTUAL CONTAMINANT LOADING:        
BLOWER HP:          HP

B6.
WARRANTY:   1-year     

B7.
PRIMARY POLLUTANTS:   NOx, CO, VOC, PM10 and SOx 

B8.
SECONDARY POLLUTANTS:   none

B9.
SPACE REQUIREMENT:   n/a

B10.
LIMITATIONS:   

B11.
LOCATION OF PRIOR DEMONSTRATION & AGENCY:
FACILITY:   California State Prison at Corcoran
CONTACT PERSON:   Pat Downey (Facilities Manager)
PHONE NO.:   (559) 992-6132
AGENCY:   San Joaquin Valley AQMD
ADDRESS:        
CONTACT PERSON:   George Heinen
PHONE NO.:   (559) 230-6000

B12.
OPERATING HISTORY:   none, construction will start 1/2000

B13.
SOURCE TEST/PERFORMANCE DATA ANALYSIS:
DATE OF SOURCE TEST:   9/5/00
CAPTURE EFFICIENCY:        
DESTRUCTION EFFICIENCY:        
OVERALL EFFICEINCY:        
PERFORMANCE DATA:        

B14.
SOURCE TEST CONDITIONS/PERFORMANCE DATA:   
 2 boilers tested:                     High                   Low

NOx, ppmvd, 3% O2          8.4/11.6               6.2/5.8 

CO, ppmvd, 3%O2                 8/2                    3/13
O2, vol. % (dry)                12.3/10.7            15.4/14.2
(Boilers operate only at two loads, high and low.)


C.
COST

C1.
CONTROL EQUIPMENT COST:
 FORMCHECKBOX 
 check if installation cost is included in capital cost
CAPITAL:   $     
INSTALLATION:   $       (
 FORMTEXT 

     
)
SOURCE OF COST DATA:   

C2.
ANNUAL OPERATIONAL/MAINTENANCE COST:    $       (
 FORMTEXT 

     
)
SOURCE OF COST DATA:   

D.
DEMONSTRATION OF COMPLIANCE

D1.
STAFF PERMFORMING FIELD EVALUATION:
ENGINEER'S NAME:        
INSPECTOR'S NAME:        
DATE:        

D2.
COMPLIANCE DEMONSTRATION:        

D3.
VARIANCE:
NO. OF VARIANCES:        
DATES:        
CAUSES:        

D4.
VIOLATION:
NO. OF VIOLATIONS:        
DATES:        
CAUSES:        

D5.
FREQUENCY OF MAINTENANCE:        

6.
COMMENTS

App. No.:   362396

Along with this application, the applicant submitted an additional application (A/N 362395) for identical equipment at the same location.



Combustion equipment form date 9/23/1999

2

2 of 3




Combustion equipment form date 5/19/1999


