Application No.:  364408

Equipment Category – Boiler - Portable

| 1. GENERAL INFORMATION |  | DATE: 6/8/2001 |
| --- | --- | --- |
| a. manufacturer: Donlee |
| b. type: portable water tube type | c. model: 582-SAHF-650-N |
| d. style: |
| e. applicable aqmd regulation xi rules: 1146 |
| f. cost: $135,000 (boiler = 60K, burner = 40K, and gas train/burner controls/trim = 35K) (2000) source of cost data: |
| g. operating schedule: 24 hrs/day 7 days/wk 52 wks/yr |

| 2. EQUIPMENT INFORMATION |  | App. No.: 364408 |
| --- | --- | --- |
| A. FUNCTION: the boiler will be used as an emergency rental unit to provide hot water and steam |
| B. maximum Heat Input: 28.8 MMbtu/hr | C. maximum throughput: |
| D. burner information: no.: 1 type: Low-NOx burner |
| e. primary fuel: natural gas | f. other fuel: LPG |
| g. operating conditions: |

| 3. COMPANY INFORMATION |  | App. No.: 364408 |
| --- | --- | --- |
| A. NAME: Nation Wide Boiler |
| B. ADDRESS: 142400 Christy Street CITY: Fremont STATE: CA ZIP: 94538 |
| C. CONTACT PERSON: Holy Lepo | D. PHONE NO.: 510-490-7100 |

| 4. PERMIT INFORMATION |  | App. No.: 364408 |
| --- | --- | --- |
| A. AGENCY: SCAQMD |
| B. AGENCY CONTACT PERSON: Roy Olivares | C. PHONE NO.: 909-393-2208 |
| D. PERMIT TO CONSTRUCT INFORMATION: P/C NO.: 364408 ISSUANCE DATE: 3/15/2000 |
| E. START-UP DATE: May 2000 |
| F. PERMIT TO OPERATE INFORMATION: P/O NO.: ISSUANCE DATE: |

| 5. EMISSION INFORMATION |  | App. No.: 364408 |
| --- | --- | --- |
| A. PERMIT |
| A1. PERMIT LIMIT: permit limits are the same for each fuel NOx = 9 ppmv, dry basis, corrected to 3% O2 CO = 50 ppmv, dry basis, corrected to 3% O2 |
| A2. bact/lAer DETERMINATION: see above limits |
| B. CONTROL TECHNOLOGY |
| B1. MANUFACTURER/SUPPLIER: ALZETA |
| B2. TYPE: Low-NOx burner, Alzeta, Model CSB22-SSO-30 |
| B3. DESCRIPTION: The premixed, natural gas fired, radiant burners operate in a flameless mode. These burners achieve low emissions by keeping the combustion temperature below 2000 degress Fahrenheit. Combustion temperature is controlled by varying excess air and surface firing rate. |
| B4. CONTROL EQUIPMENT PERMIT APPLICATION DATA: P/C NO.: na ISSUANCE DATE: P/O NO.: na ISSUANCE DATE: |
| B5. WASTE AIR FLOW TO CONTROL EQUIPMENT: FLOW RATE: na ACTUAL CONTAMINANT LOADING: BLOWER HP: HP |
| B6. WARRANTY: |
| B7. PRIMARY POLLUTANTS: NOx, CO, VOC, PM10, and SOx |
| B8. SECONDARY POLLUTANTS: none |
| B9. SPACE REQUIREMENT: na |
| B10. LIMITATIONS: na |
| B11. LOCATION OF PRIOR DEMONSTRATION & AGENCY: FACILITY: UCI Medical Center CONTACT PERSON: David Mori PHONE NO.: (714) 456-6738 AGENCY: SCAQMD ADDRESS: 21865 E. Copley Drive CONTACT PERSON: Knut Beruldsen PHONE NO.: (909) 396-3136 |
| B12. OPERATING HISTORY: Construction started 1/2000 |
| B13. SOURCE TEST/PERFORMANCE DATA ANALYSIS: DATE OF SOURCE TEST: 7/7/00 CAPTURE EFFICIENCY: DESTRUCTION EFFICIENCY: OVERALL EFFICEINCY: PERFORMANCE DATA: |
| B14. SOURCE TEST CONDITIONS/PERFORMANCE DATA: Results for 2 boilers; high, avg., low loads: High Avg. Low NOx, ppmvd, 3% O2 6.7 5.2 4.5 CO, ppmvd, 3%O2 <28 <29 <32 O2, vol. % (dry) 8.1 8.7 9.5 |
| C. COST |
| C1. CONTROL EQUIPMENT COST: check if installation cost is included in capital cost CAPITAL: $40,000 INSTALLATION: $ (2000) SOURCE OF COST DATA: |
| C2. ANNUAL OPERATIONAL/MAINTENANCE COST: $ ( ) SOURCE OF COST DATA: |
| D. DEMONSTRATION OF COMPLIANCE |
| D1. STAFF PERMFORMING FIELD EVALUATION: ENGINEER'S NAME: INSPECTOR'S NAME: DATE: |
| D2. COMPLIANCE DEMONSTRATION: |
| D3. VARIANCE: NO. OF VARIANCES: DATES: CAUSES: |
| D4. VIOLATION: NO. OF VIOLATIONS: DATES: CAUSES: |
| D5. FREQUENCY OF MAINTENANCE: |

| 6. COMMENTS |  | App. No.: 364408 |
| --- | --- | --- |
| The operator is required by permit condition to inspect and maintain the ultra low-NOx burner in accordance with manufacturer's specifications. The boiler will be operated at various locations within the SCAQMD. This BACT determination is based on the operation of a 48.6 MMbtu/hour boiler with a 9 ppm NOx limit at UCI Medical Center in Orange, California (A/N 248532), equipped with an Alzeta ceramic fiber radiant burner. That unit has been in operation since 1993, and a review of the CEMS data indicates compliance with the 9 ppm permit limit. This boiler is equipped with a similar burner from Alzeta that is also capable of complying with a 9 ppm limit. |