Application No.:  385770

Equipment Category - Boiler

| 1. GENERAL INFORMATION |  | DATE: 11/22/2002 |
| --- | --- | --- |
| a. manufacturer: Clayton Industries |
| b. type: Water Tube | c. model: EG504-1-FMB |
| d. style: |
| e. applicable aqmd rules: 1146, 401, 402, 404, 407, 409, 431.1 |
| f. cost: $ () source of cost data: |
| g. operating schedule: 24 hrs/day 5 days/wk 52 wks/yr |

| 2. EQUIPMENT INFORMATION |  | App. No.: 385770 |
| --- | --- | --- |
| A. FUNCTION: Process steam for cosmetics manufacturing processes. |
| B. maximum Heat Input: 21.46 MMBtu.hr | C. maximum throughput: |
| D. burner information: no.: 1 type: Ultra Low-NOx |
| e. primary fuel: Natural Gas | f. other fuel: None |
| g. operating conditions: Variable load |

| 3. COMPANY INFORMATION |  | App. No.: 385770 |
| --- | --- | --- |
| A. NAME: Cosmetic Laboratories | B. SIC CODE: 2844 |
| C. ADDRESS: 20245 Sunburst Street CITY: Chatsworth STATE: CA ZIP: 91311 |
| D. CONTACT PERSON: Larry Magcale | E. PHONE NO.: 818-998-3511 |

| 4. PERMIT INFORMATION |  | App. No.: 385770 |
| --- | --- | --- |
| A. AGENCY: SCAQMD | B. application type: |
| C. AGENCY CONTACT PERSON: Francisco Escobar | D. PHONE NO.: 909-396-2503 |
| E. PERMIT TO CONSTRUCT/OPERATE INFORMATION: P/C NO.: 385770 (A/N) ISSUANCE DATE: 9/4/2001 check if no p/c P/O NO.: F49930 ISSUANCE DATE: 3/12/2002 |
| F. START-UP DATE: Early April 2002 (The Permit to Operate was issued early in this case; however, it contains a condition requiring a source test within 180 days after startup showing compliance.) |

| 5. EMISSION INFORMATION |  | App. No.: 385770 |
| --- | --- | --- |
| A. PERMIT |
| A1. PERMIT LIMIT: 9 ppm NOx (dry, 3% O2) and 100 ppm CO (dry, 3% O2). |
| A2. bact/lAer DETERMINATION: Low-NOx burner meeting 9 ppm NOx and 100 ppm CO (both dry basis, corrected to 3% O2) |
| a3. BASIS OF THE BACT/LAER DETERMINATION: AQMD BACT Guidelines |
| B. CONTROL TECHNOLOGY |
| B1. MANUFACTURER/SUPPLIER: Clayton Industries |
| B2. TYPE: Ultra Low-NOx Burner |
| B3. DESCRIPTION: Model UK-30672 high-air, premix, metal fiber burner. |
| B4. CONTROL EQUIPMENT PERMIT APPLICATION DATA: P/C NO.: ISSUANCE DATE: P/O NO.: ISSUANCE DATE: |
| B5. WASTE AIR FLOW TO CONTROL EQUIPMENT: FLOW RATE: ACTUAL CONTAMINANT LOADING: BLOWER HP: |
| B6. WARRANTY: |
| B7. PRIMARY POLLUTANTS: NOx, CO, PM, SOx |
| B8. SECONDARY POLLUTANTS: None |
| B9. SPACE REQUIREMENT: |
| B10. LIMITATIONS: | B11. UNUSED |
| B12. OPERATING HISTORY: Has been in regular service since startup with no problems. |
| B13. UNUSED | B14. UNUSED |
| C. CONTROL EQUIPMENT COSTS |
| C1. CAPITAL COST: check if installation cost is included in EQUIPMENT cost EQUIPMENT: $ INSTALLATION: $ () SOURCE OF COST DATA: |
| C2. ANNUAL OPERATING COST: $ () SOURCE OF COST DATA: |
| D. DEMONSTRATION OF COMPLIANCE |
| D1. STAFF PERMFORMING FIELD EVALUATION: ENGINEER'S NAME: INSPECTOR'S NAME: Tom Rooney DATE: 6/28/2002 |
| D2. COMPLIANCE DEMONSTRATION: |
| D3. VARIANCE: NO. OF VARIANCES: None DATES: CAUSES: |
| D4. VIOLATION: NO. OF VIOLATIONS: None DATES: CAUSES: |
| D5. MAINTENANCE REQUIREMENTS: Permit requires that tune-up and maintenance instructions provided by manufacturer be followed to keep emissions in compliance. | D6. UNUSED |
| D7. SOURCE TEST/PERFORMANCE DATA RESULTS AND ANALYSIS: DATE OF SOURCE TEST: 4/23/2002 CAPTURE EFFICIENCY: DESTRUCTION EFFICIENCY: OVERALL EFFICIENCY: SOURCE TEST/PERFORMANCE DATA: Test Condition High Fire Low Fire Normal Load, % 100 25 Varying O2, % (dry) 9.4 11.3 10.3 NOx, ppm (dry, 3% O2) 6.2 5.1 4.6 CO, ppm (dry, 3% O2) <31 <37 <34 Source test accepted by AQMD Monitoring & Source Test Engineering group. OPERATING CONDITIONS: High, low and normal (load-following) TEST METHODS: AQMD Method 100.1 |

| 6. COMMENTS |  | App. No.: 385770 |
| --- | --- | --- |
| AQMD unannounced emissions test 6/28/2002 using portable analyzer found 10 ppm NOx and 2 ppm CO (dry, corrected to 3% O2). NOx was considered to be in compliance with the 9 ppm limit in view of the relatively coarse accuracy of the test method. Clayton offers this ultra low-NOx burner in its boilers rated at 400 to 600 hp, and now guarantees it to meet AQMD NOx and CO requirements. |