Application No.:  99-PO-01

Equipment Category – Gas Turbine

| 1. GENERAL INFORMATION |  |  | DATE: 12/18/2001 |
| --- | --- | --- | --- |
| a. manufacturer: GE or Westinghouse |  |  |  |
| b. type: Combined Cycle |  | c. model: GE PG7241FA or Westinghouse 501F |  |
| d. style: Includes inlet air evaporative cooling |  |  |  |
| e. applicable aqmd regulation xi rules: |  |  |  |
| f. cost: $ () source of cost data: |  |  |  |
| g. operating schedule: 24 hrs/day 7 days/wk 52 wks/yr |  |  |  |

| 2. EQUIPMENT INFORMATION |  |  | App. No.: 99-PO-01 |
| --- | --- | --- | --- |
| A. FUNCTION: Power Generation (one of two identical gas turbine/HRSG units sharing common steam turbine). Capacity per gas turbine: 170 MW. Capacity of steam turbine: 230 MW. |  |  |  |
| B. maximum Heat Input: 2,038 MMBtu/hr (Est. based on Mountainview and Elk Hills cases), plus 290 MMBtu/hr to HRSG duct burners |  | C. maximum throughput: |  |
| D. burner information: no.: type: Turbine has dry low-NOx burners. Duct burners are low-NOx. |  |  |  |
| e. primary fuel: Natural Gas |  | f. other fuel: |  |
| g. operating conditions: |  |  |  |

| 3. COMPANY INFORMATION |  |  | App. No.: 99-PO-01 |  |
| --- | --- | --- | --- | --- |
| A. NAME: Three Mountain Power, LLC |  |  |  | B. SIC CODE: |
| C. ADDRESS: c/o Ogden Power Pacific, Inc., 3085 Crossroads Dr. CITY: Redding STATE: CA ZIP: 96003 |  |  |  |  |
| D. CONTACT PERSON: Martin McFadden |  | E. PHONE NO.: |  |  |

| 4. PERMIT INFORMATION |  |  |  | App. No.: 99-PO-01 |
| --- | --- | --- | --- | --- |
| A. AGENCY: Shasta County AQMD |  | B. application type: |  |  |
| C. AGENCY CONTACT PERSON: Rita Cirulis |  |  | D. PHONE NO.: 530-225-5156 |  |
| E. PERMIT TO CONSTRUCT/OPERATE INFORMATION: P/C NO.: 99-PO-01 ISSUANCE DATE: 10/10/2000 check if no p/c P/O NO.: ISSUANCE DATE: |  |  |  |  |
| F. START-UP DATE: January 2004 |  |  |  |  |

| 5. EMISSION INFORMATION |  |  | App. No.: 99-PO-01 |  |  |
| --- | --- | --- | --- | --- | --- |
| A. PERMIT |  |  |  |  |  |
| A1. PERMIT LIMIT: PPM (dry @ 15% O2): NOx-2.5(1-hr)(2.5 will be changed to 2.0 subject to a 3-yr demo. period), CO-4(3-hr), VOC-2(1-hr), NH3-5(3-hr); PM: .0012 gr/dscf@3%CO2(1-hr). Max. S in fuel: 0.4 gr/100 SCF. Daily and annual mass limits on PM10, NOx, CO, VOC, SOx. |  |  |  |  |  |
| A2. bact/lAer DETERMINATION: The limits on NOx, CO, VOC and NH3 as well as the limit on fuel sulfur content were all believed to represent BACT for this source category. |  |  |  |  |  |
| a3. BASIS OF THE BACT/LAER DETERMINATION: NOx: 2.5 ppm (1-hr) NOx limit is consistent with the CARB "Guidelines for Power Plant Sitings" document; 2.0 ppm subject to demonstration period was proposed by the applicant. The CO limit was proposed by the applicant. The VOC limit is consistent with the CARB guidelines. The 0.4 gr/100 scf limit on fuel sulfur was recommended by CEC. |  |  |  |  |  |
| ##### B. CONTROL TECHNOLOGY |  |  |  |  |  |
| B1. MANUFACTURER/SUPPLIER: Engelhard |  |  |  |  |  |
| B2. TYPE: SCR System plus Oxidation Catalyst |  |  |  |  |  |
| B3. DESCRIPTION: Aqueous ammonia is used (19% solution). |  |  |  |  |  |
| B4. CONTROL EQUIPMENT PERMIT APPLICATION DATA: P/C NO.: 99-PO-01 ISSUANCE DATE: 10/10/2001 P/O NO.: ISSUANCE DATE: |  |  |  |  |  |
| B5. WASTE AIR FLOW TO CONTROL EQUIPMENT: FLOW RATE: ACTUAL CONTAMINANT LOADING: BLOWER HP: |  |  |  |  |  |
| B6. WARRANTY: 2.0 ppm NOx (dry, 15% O2) guaranteed for 3 years. |  |  |  |  |  |
| B7. PRIMARY POLLUTANTS: NOx, CO, VOC, PM, SOx |  |  |  |  |  |
| B8. SECONDARY POLLUTANTS: NH3 |  |  |  |  |  |
| B9. SPACE REQUIREMENT: |  |  |  |  |  |
| B10. LIMITATIONS: Min. temperature for NH3 injection is 500 F. |  |  |  | ###### B11. UNUSED |  |
| B12. OPERATING HISTORY: |  |  |  |  |  |
| ### B13. UNUSED |  | ### B14. UNUSED |  |  |  |
| ##### C. CONTROL EQUIPMENT COSTS |  |  |  |  |  |
| C1. CAPITAL COST: check if installation cost is included in EQUIPMENT cost EQUIPMENT: $ INSTALLATION: $ () SOURCE OF COST DATA: |  |  |  |  |  |
| C2. ANNUAL OPERATING COST: $ () SOURCE OF COST DATA: |  |  |  |  |  |
| D. DEMONSTRATION OF COMPLIANCE |  |  |  |  |  |
| D1. STAFF PERMFORMING FIELD EVALUATION: ENGINEER'S NAME: INSPECTOR'S NAME: DATE: |  |  |  |  |  |
| D2. COMPLIANCE DEMONSTRATION: CEMS for NOx and CO. Annual source test for NH3. |  |  |  |  |  |
| D3. VARIANCE: NO. OF VARIANCES: DATES: CAUSES: |  |  |  |  |  |
| D4. VIOLATION: NO. OF VIOLATIONS: DATES: CAUSES: |  |  |  |  |  |
| D5. MAINTENANCE REQUIREMENTS: Periodic catalyst replacement/refurbishment. Ammonia storage, handling, injection system maintenance. |  |  |  |  | D6. UNUSED |
| D7. SOURCE TEST/PERFORMANCE DATA RESULTS AND ANALYSIS: DATE OF SOURCE TEST: Within 60 days after startup CAPTURE EFFICIENCY: DESTRUCTION EFFICIENCY: OVERALL EFFICEINCY: SOURCE TEST/PERFORMANCE DATA: OPERATING CONDITIONS: TEST METHODS: |  |  |  |  |  |

| 6. COMMENTS |  | App. No.: 99-PO-01 |
| --- | --- | --- |
| It is significant that the permit NOx level accepted by the applicant is the same regardless of whether the gas turbine selected is a GE F7A or a Westinghouse 501F, which generally operates at a higher NOx level. It should be noted that the permit emission limits have not yet been verified by performance data. |  |  |