## Criteria Pollu. Emissions
DWP VALLEY STATION -- CRITERIA POLLUTANT EMISSIONS
NORMAL OPERATION
Natural Gas Use by the Combustion Turbine
Device ID Number: | Combustion Turbine #1
Process Description:
No. of Devices: | 1
Process Equipment Description: | GE LM6000, Sprint 47.3 MW
Fuel Type: | Natural Gas
Process Units: | MMSCF
Control Equipment: | Selective Catalytic Reduction, CO Catalyst, and
water-steam injection
Yearly Emis. Est. Equation: | Fy x EF
Max Hourly Emis. Est. Equation: | Fm x EF
Parameter Symbols/Names |  |  | Values
Fy = Total Yearly Amount of Fuel Burned (one CT) |  |  | 3582.8 | MMSCF
Fm = Maximum Hourly Amount of Fuel Burned (one CT) |  |  | 0.409 | MMSCF
EF = Emission Factor |  |  | See below | lbs/MMSCF
Process Operation Schedule |  |  | 24 | hours/day
|  |  | 7 | days/week
|  |  | 52 | weeks/year
Criteria | Emission | Hourly Max | Annual | Annual | Daily
Species Name | Factor | Emissions | Emissions | Emissions | Emissions
| (lb/MMscf) | (lbs/hr) | (lbs/yr) | (tons/yr) | (lbs/day)
NOx | 19.64 | 8.03 | 70366 | 35.18 | 192.72
CO | 14.39 | 5.89 | 51556 | 25.78 | 141.36
VOC | 2.73 | 1.12 | 9781 | 4.89 | 26.88
NH3 | 7.25 | 2.97 | 25975 | 12.99 | 71.28
PM10 | 6.93 | 2.83 | 24829 | 12.41 | 67.92
PM10 conversion of SO2 to SO3 | 0.152 | 0.06 | 544.59 | 0.27 | 1.44
Total PM10 | NA | 2.89 | 25373.59 | 12.68 | 69.36
SO2 | 1.48 | 0.61 | 5303 | 2.65 | 14.64
Criteria | Hourly Max
Species Name | Hrly Emissions
(grams/sec)
NOx | 1.013
CO | 0.743
VOC | 0.141
NH3 | 0.375
PM10 | 0.357
PM10 conversion of SO2 to SO3 | 0.008
Total PM10 | 0.364
SO2 | 0.077

## Air Toxics Emissions
DWP VALLEY STATION -- AIR TOXICS EMISSIONS
NORMAL OPERATIONS
Natural Gas Use by the Combustion Turbine
Device ID Number: |  | Combustion Turbine #1
Process Description:
No. of Devices: |  | 1 (1)
Process Equipment Description: |  | GE LM6000, Sprint 47.3 MW
Fuel Type: |  | Natural Gas
Process Units: |  | MMCF
Control Equipment: |  | Selective Catalytic Reduction and CO Catalyst
Yearly Emis. Est. Equation: |  | Fy x EF
Max Hourly Emis. Est. Equation: |  | Fm x EF
Parameter Symbols/Names
Fy = Total Yearly Amount of Fuel Burned (one CT) |  |  | 3582.8 | MMCF
Fm = Maximum Hourly Amount of Fuel Burned (one CT) |  |  | 0.409 | MMCF
EF = Emission Factor2,3 |  |  | See below | lbs/MMCF
Process Operation Schedule |  |  | 24 | hours/day
|  |  | 7 | days/week
|  |  | 52 | weeks/year
| Air Toxic | Emission | Hourly Max | Annual | Annual
Air Toxic | CAS Number | Factor | Emissions | Emissions | Emissions
|  | (lb/MMscf) | (lbs/hr) | (lbs/yr) | (tons/yr)
1,3-Butadiene | 106990 | 0.000127 | 5.1943e-05 | 0.45502 | 0.00022751
Acetaldehyde | 75070 | 0.137 | 0.056033 | 490.8436 | 0.24542
Acrolein | 107028 | 0.0189 | 0.0077301 | 67.7149 | 0.033857
Ammonia | 7664417 | 7.25 | 2.9652 | 25975.3 | 12.99
Benz(a)anthracene (PAH) | 56553 | 2.26e-05 | 9.2434e-06 | 0.080971 | 4.0486e-05
Benzene | 71432 | 0.0133 | 0.0054397 | 47.6512 | 0.023826
Benzo(a)pyrene (PAH) | 50328 | 1.39e-05 | 5.6851e-06 | 0.049801 | 2.49e-05
Benzo(b)fluoranthene (PAH) | 205992 | 1.13e-05 | 4.6217e-06 | 0.040486 | 2.0243e-05
Benzo(k)fluoranthene (PAH) | 207089 | 1.1e-05 | 4.499e-06 | 0.039411 | 1.9705e-05
Chrysene (PAH) | 218019 | 2.52e-05 | 1.0307e-05 | 0.090287 | 4.5143e-05
Dibenz(a,h)anthracene (PAH) | 53703 | 2.35e-05 | 9.6115e-06 | 0.084196 | 4.2098e-05
Ethylbenzene | 100414 | 0.0179 | 0.0073211 | 64.1321 | 0.032066
Formaldehyde | 50000 | 0.917 | 0.37505 | 3285.4276 | 1.6427
Hexane | 110543 | 0.259 | 0.10593 | 927.9452 | 0.46397
Indeno(1,2,3-cd)pyrene (PAH) | 193395 | 2.35e-05 | 9.6115e-06 | 0.084196 | 4.2098e-05
Naphthalene (PAH) | 91203 | 0.00166 | 0.00067894 | 5.9474 | 0.0029737
Propylene | 115071 | 0.771 | 0.31534 | 2762.3388 | 1.3812
Propylene Oxide | 75569 | 0.0478 | 0.01955 | 171.2578 | 0.085629
Toluene | 108883 | 0.071 | 0.029039 | 254.3788 | 0.12719
Xylene(Total) | 1330207 | 0.0261 | 0.010675 | 93.5111 | 0.046756
1. One new combustion turbine will be installed at the Valley facility.
2. Mean Emission factors for all the air toxics except for ammonia are from the latest California Air
Resources Board's (CARB) air toxics emission data base. The emission factors were provided by
CARB to Parsons Engineering Science on 10/12/00.
3. The emissions are quantified for only those air toxics which are listed in Table 1 of the SCAQMD's
Rule 1401 (Amended August 2000).

## Air Toxics Grams per second
DWP VALLEY STATION -- AIR TOXICS EMISSIONS IN GRAMS/SECOND
NORMAL OPERATIONS
Natural Gas Use by the Combustion Turbine
Device ID Number: |  | Combustion Turbine #1
Process Description:
No. of Devices: |  | 1 (1)
Process Equipment Description: |  | GE LM6000, Sprint 47.3 MW
Fuel Type: |  | Natural Gas
Process Units: |  | MMCF
Control Equipment: |  | Selective Catalytic Reduction and CO Catalyst
Yearly Emis. Est. Equation: |  | Fy x EF
Max Hourly Emis. Est. Equation: |  | Fm x EF
Parameter Symbols/Names
Fy = Total Yearly Amount of Fuel Burned (one CT) |  |  | 3582.8 | MMCF
Fm = Maximum Hourly Amount of Fuel Burned (one CT) |  |  | 0.409 | MMCF
EF = Emission Factor2,3 |  |  | See below | lbs/MMCF
Process Operation Schedule |  |  | 24 | hours/day
|  |  | 7 | days/week
|  |  | 52 | weeks/year
| Air Toxic | Emission | Hourly Max | Hourly Max
Air Toxic | CAS Number | Factor | Emissions | Emissions
|  | (lb/MMscf) | (lbs/hr) | (grams/second)
1,3-Butadiene | 106990 | 0.000127 | 5.1943e-05 | 6.5506e-06
Acetaldehyde | 75070 | 0.137 | 0.056033 | 0.0070664
Acrolein | 107028 | 0.0189 | 0.0077301 | 0.00097485
Ammonia | 7664417 | 7.25 | 2.9652 | 0.37395
Benz(a)anthracene (PAH) | 56553 | 2.26e-05 | 9.2434e-06 | 1.1657e-06
Benzene | 71432 | 0.0133 | 0.0054397 | 0.00068601
Benzo(a)pyrene (PAH) | 50328 | 1.39e-05 | 5.6851e-06 | 7.1695e-07
Benzo(b)fluoranthene (PAH) | 205992 | 1.13e-05 | 4.6217e-06 | 5.8285e-07
Benzo(k)fluoranthene (PAH) | 207089 | 1.1e-05 | 4.499e-06 | 5.6737e-07
Chrysene (PAH) | 218019 | 2.52e-05 | 1.0307e-05 | 1.2998e-06
Dibenz(a,h)anthracene (PAH) | 53703 | 2.35e-05 | 9.6115e-06 | 1.2121e-06
Ethylbenzene | 100414 | 0.0179 | 0.0073211 | 0.00092327
Formaldehyde | 50000 | 0.917 | 0.37505 | 0.047298
Hexane | 110543 | 0.259 | 0.10593 | 0.013359
Indeno(1,2,3-cd)pyrene (PAH) | 193395 | 2.35e-05 | 9.6115e-06 | 1.2121e-06
Naphthalene (PAH) | 91203 | 0.00166 | 0.00067894 | 8.5622e-05
Propylene | 115071 | 0.771 | 0.31534 | 0.039768
Propylene Oxide | 75569 | 0.0478 | 0.01955 | 0.0024655
Toluene | 108883 | 0.071 | 0.029039 | 0.0036621
Xylene(Total) | 1330207 | 0.0261 | 0.010675 | 0.0013462
1. One new combustion turbine will be installed at the Valley facility.
2. Mean Emission factors for all the air toxics except for ammonia are from the latest California Air
Resources Board's (CARB) air toxics emission data base. The emission factors were provided by
CARB to Parsons Engineering Science on 10/12/00.
3. The emissions are quantified for only those air toxics which are listed in Table 1 of the SCAQMD's
Rule 1401 (Amended August 2000).

## EF Criteria
DEVELOPMENT OF CRITERIA POLLUTANT EMISSON FACTORS
FOR COMBUSTION TURBINE AT THE VALLEY PLANT
(Natural Gas Use by the Combustion Turbine)
1. The new combustion turbine (CT) is GE LM6000 Sprint 47.3 MW (47,300 kW) turbine(1).
2. The heating input required is 8250 Btu/kW-hr (LHV), LM6000 GTG specifications(1).
3. The CT will use natural gas with a HHV of 1050 Btu/scf (2).
4. Emission limits are 5 ppmv for oxides of nitrogen (NOx), 6 ppmv for carbon monoxide (CO),
2 ppmv for volatile organic compounds (VOC), and 5 ppmv for ammonia (NH3)(6).
5. Emission limits are assumed to be at 15% O2.
6. The CT will be provided with SCR, CO Catalyst, and water-steam injection.(1)
Calculate Molecular Weight of Natural Gas
| Compound | Mole% (2) | MW | Weighted MW
| methane | 94 | 16 | 15
| ethane | 3 | 30 | 0.9
| propane | 2 | 44 | 0.9
| CO2 | 1 | 44 | 0.4
| Total |  |  | 17.2
Calculate Maximum Firing Rate (MFR) for the CT in Btu/hr
Maximum Firing Rate = 47,300 kW X 8250 Btu/kW-hr
MFR | Size | Factor | LHV | HHV
(Btu/hr) | (kW) | (Btu/kW-hr) | (Btu/scf) | (Btu/scf)
390225000 | 47300 | 8250 | 953 | 1050
Maximum Hourly Fuel Consumption Rate (MMcf) = MFR/(LHV x 1,000,000)
Maximum Hourly Fuel Consumption Rate (MMcf) = |  |  |  | 0.409 | MMcf/hr
Maximum Annual Fuel Consumption = Maximum Hourly Rate x 8760 hours/yr
(It is assumed that the turbine operates continuously at full capacity throughout the year.)
Maximum Annual Fuel Consumption = |  |  | 3582.8 | MMcf/yr
Convert Emission Limits (EL) from ppmv to lb/MMBtu for NOx, CO, VOC, and NH3.
EL (lbs/MMBtu) = Exhaust Volume x Concentration x MW of Pollutant (3)
1,000,000 x 379
Exhaust Volume (DSCF/MMBtu) = 8710 DSCF/MMBtu x 20.9/(20.9 -%O2) (7)
Pollutant | Oxygen | Exhaust Vol | Conc. | MW | Fuel | EL
| (%) | (DSCF/MMBtu) | (ppmv) | (lb/lb-mole) | (MMSCFH) | (lb/MMBtu)
NOx (NO2) | 15 | 30854.0678 | 5 | 46 | 0.409 | 0.0187
CO | 15 | 30854.0678 | 6 | 28 | 0.409 | 0.0137
VOC (CH4) | 15 | 30854.0678 | 2 | 16 | 0.409 | 0.0026
NH3 | 15 | 30854.0678 | 5 | 17 | 0.409 | 0.0069
Convert Emission Limit (EL) in lb/MMBtu to Emission Factor in lb/MMscf, EF = EL x HHV (Btu/scf)
| Pollutant | EL | HHV | EF
|  | (lb/MMBtu) | (Btu/scf) | (lb/MMscf)
| NOx (NO2) | 0.0187 | 1050 | 19.64
| CO | 0.0137 | 1050 | 14.39
| VOC (CH4) | 0.0026 | 1050 | 2.73
| NH3 | 0.0069 | 1050 | 7.25
Emission Factors for PM10 and Sulfur Dioxide (SO2)
| Pollutant | Emission | HHV | Emission | Sulfur
|  | Factor | (Btu/scf) | Factor
|  | (lb/MMBtu) |  | (lb/MMscf) | (wt%)
| PM10 (4) | 0.0066 | 1050 | 6.93 | NA
| SO2 (5) | 0.94S | 1050 | 1.48 | 0.0015
Sulfur in Natural Gas (S)
WT% S = 100 x S in ppmv in natural gas x MW of S /(MW of Natural Gas x 106)
|  | S in ppmv (2) | MW of S | MW of Natural Gas (2) | WT% S
|  | 8 | 32 | 17.2 | 0.0015
Calculate PM10 from Conversion of SO2 to ammonium sulfate
SO2 to SO3 = 5% molar conversion (8)
SO3 to ammonium sulfate: 1 mole SO3 = 1 mole of ammonium sulfate (8)
| SO2 | SO2 | SO3 | PM10 | PM10
| (lbs/BTU) | (lb-mole/MMBtu) | (lb-mole/MMBtu) | (lb/MMBtu) | (lbs/MMscf)
| 0.0014 | 2.1875e-05 | 1.0938e-06 | 0.00014459 | 0.152
(1) Specification provided by LA DWP from Request for Proposal dated September 25, 2000 and
and S & S Energy Products' Specifications sheet.
(2) SCR Bid specification (no. 9628) from LA DWP. Natural gas LHV calculated to be 953 Btu/scf.
Maximum value for sulfur in natural gas selected.
(3) Taken from SCAQMD Title V Technical Guidance Manual, page A-20, 1998.
(4) Emission factor in lb/MMBtu is from Ap-42, Table 3.1-2a.
(5) Emission Factor in lb/MMBtu is from AP-42, Table 3.1-2a.
(6) Specifications from LA DWP (Generation - 2000 Project Overview)
(7) EPA Method 19, 40 CFR Part 60.
(8) SCAQMD Application Processing and Calculations, Energy Team, 10-14-93. Faxed to Krishna Nand on 11-17-00.

## stack
DEVELOPMENT OF THE STACK GAS FLOW RATE
FOR THE COMBUSTION TURBINE AT THE VALLEY PLANT
(Natural Gas Use by the Combustion Turbine)
1. The Valley Plant will have one new Combustion Turbine with a capacity of 47.3 mW. (1)
2. The stack gas flow rate for the CT ranges from 929,950 lbs/hr (summer: 854,950 + 75,000) to
1,054,800 lbs/hr (winter). (2)
3. The stack gas temperature will average 824 oF. (2)
4. The assumed stack gas O2 content is 15%.
5. The assumed stack gas molecular weight is 28.
6. Standard temperature is assumed to be 60 oF.
7. The stack gas flow rates provided are assumed to include water.
8. The stack gas flows in SCFH and ACFH will be based on the average of the mass flow rates.
Calculate the Stack Gas Flow Rate
Stack Gas Flow Rate, SCFH = |  | Stack Gas Flow (lbs/hr) x 379 (scf/lb-mole)
MW (lbs/lb-mole)
Stack Gas Flow Rate, ACFH = |  | Stack Gas Flow (SCFH) x |  | [Stack Gas Temp (oR)]
[Standard Temp (oR)]
Winter Mass Flow = |  | 1054800 | lbs/hr | Summer Mass Flow = |  | 929950 | lbs/hr
Average Mass Flow = |  | 992375 | lbs/hr | Average Temperature = |  | 824 | oF
UNIT | Average Stack Gas Flow | Stack Gas MW | Stack Gas Temp | Stack Gas Flow | Stack Gas Flow | Stack Gas Flow | Stack Gas Flow
| (lbs/hr) | (lb/lb-mole) | (oF) | (SCFH) | (ACFH) | (SCFM) | (ACFM)
CT #1 | 992375 | 28 | 824 | 13432504 | 33167952 | 223875 | 552799
Unit | Stack Inside Diameter(2) | Stack Exit Velocity | Stack Exit Velocity | Stack Inside Diameter | Stack Height(2) | Stack Height
| (FT) | (FT/SEC) | (M/SEC) | (M) | (FT) | (M)
CT #1 | 10 | 117.31 | 35.76 | 3.05 | 110 | 33.53
(1) Information provided by LA DWP.
(2) Information from LA DWP in e-mail from Tim Conkin dated 10/18/00.

## Air Toxics EF
CARB AIR TOXICS EMISSION FACTORS
COMBUSTION TURBINES -- NATURAL GAS
Air Toxics Emission factors are from California Air Resources Board's latest air toxics data
base. These emission factors are for combustion turbines equipped with SCR and CO
catalysts. The data were provided by CARB on 10/12/00 (fax from Kirk Rosenkranz to Krishna
Nand Tel. No. 916/322-7673).
Substance | Air Toxic | CAS No. | Rule 1401 | Mean Emission
Category |  |  | Listed Air | Factor
|  |  | Toxic (Y/N) | (lbs/MMSCF)
VOC | 1,3-Butadiene | 106990 | Y | 0.000127
SVOC | 2-Chloronaphthalene | 91587 | N | 2.72e-07
SVOC | 2-Methylnaphthalene | 91576 | N | 5.29e-06
PAH | Acenaphthene (PAH) | 83329 | N | 1.9e-05
PAH | Acenaphthylene (PAH) | 208968 | N | 1.47e-05
VOC | Acetaldehyde | 75070 | Y | 0.137
VOC | Acrolein | 107028 | Y | 0.0189
PAH | Anthracene (PAH) | 120127 | N | 3.38e-05
PAH | Benz(a)anthracene (PAH) | 56553 | Y | 2.26e-05
VOC | Benzene | 71432 | Y | 0.0133
PAH | Benzo(a)pyrene (PAH) | 50328 | Y | 1.39e-05
PAH | Benzo(b)fluoranthene (PAH) | 205992 | Y | 1.13e-05
PAH | Benzo(e)pyrene (PAH) | 192972 | N | 5.44e-07
PAH | Benzo(g,h,i)perylene (PAH) | 191242 | N | 1.37e-05
PAH | Benzo(k)fluoranthene (PAH) | 207089 | Y | 1.1e-05
PAH | Chrysene (PAH) | 218019 | Y | 2.52e-05
PAH | Dibenz(a,h)anthracene (PAH) | 53703 | Y | 2.35e-05
SVOC | Ethylbenzene | 100414 | Y | 0.0179
PAH | Fluoranthene (PAH) | 206440 | N | 4.32e-05
PAH | Fluorene (PAH) | 86737 | N | 5.8e-05
VOC | Formaldehyde | 50000 | Y | 0.917
VOC | Hexane | 110543 | Y | 0.259
PAH | Indeno(1,2,3-cd)pyrene (PAH) | 193395 | Y | 2.35e-05
PAH | Naphthalene (PAH) | 91203 | Y | 0.00166
SVOC | Perylene | 198550 | N | 7e-07
PAH | Phenanthrene (PAH) | 85018 | N | 0.000313
VOC | Propylene | 115071 | Y | 0.771
VOC | Propylene Oxide | 75569 | Y | 0.0478
PAH | Pyrene (PAH) | 129000 | N | 2.77e-05
VOC | Toluene | 108883 | Y | 0.071
VOC | Xylene(Total) | 1330207 | Y | 0.0261